ELECTRIC REMOTE HIGH FLOW MASTER STREAM NOZZLE

Task Force Tips Master Stream 4000 series, model # MT-A4ER-FX remote electrically controlled pattern, automatic master stream nozzle shall be provided. For corrosion resistance, the nozzle shall be constructed for lightweight hardcoat anodized aluminum. The electric drive unit shall be enclosed in a waterproof housing and include a manual override device in the event the power source fails. The unit shall be compatible with 12 or 24-volt power systems and require no more than a 5-amp peak and 3-amp nominal current draw and include a waterproof connection cable with plug. Electrical actuator systems shall have a rating of IP66/IP67 per IEC 65029.

The nozzle shall have a flow range of 600 to 4000 GPM with an adjustable pressure operating range from 80 to 120 PSI. The pressure adjustment control knob shall be located at the front of the nozzle. The nozzle shall maintain constant pressure throughout the flow range and deliver a variable stream pattern from straight to wide fog.

The nozzle shall be configured with a 6” ANSI 150 flange inlet to Task Force Tips Tsunami monitor quick connect to allow other Tsunami quick connect nozzles to be installed on the 6” ANSI 150 flange. The nozzle shall have a unique serial number and be covered by a five-year warranty.