IN-LINE FOAM EDUCTOR

Task Force Tips model # UEP-450-BHBH in line foam eductor shall be provided. The portable in line foam eductor shall be constructed of corrosion resistant, hardcoat anodized aluminum alloy with stainless steel components. The foam concentrate pickup tube shall be 900 mm (36”) in length and constructed of 25 mm (1") inside diameter, reinforced transparent tubing attached to a 400 mm (16”) long stainless steel pickup tube. A back-flush pushbutton control shall be provided for fast cleaning of the unit and all controls shall be designed for use with gloved hands. The unit shall have a unique serial number and be covered by a five-year warranty.

The device shall be calibrated to proportion Class A or B foams in the following percentages: 0.25%, 0.50%, 1.0%, 3.0% and 6.0%.

The eductor shall be configured with a 2" male BSP rigid thread and 2" male BSP rigid thread and be rated for a 450 LPM foam solution discharge at inlet pressure of 10 BAR.