OSCILLATING PORTABLE ATTACK MONITOR PACKAGE

Task Force Tips Blitzfire OSC model # XXC-33NB-NH1 oscillating portable lightweight attack monitor package comprising of oscillating monitor and Max Series nozzle tip shall be supplied.

The package shall be configured as follows:

Task Force Tips Blitzfire oscillating portable lightweight attack monitor model number XX211A shall be supplied. The water powered turbine shall allow the nozzle to automatically sweep 10, 15 or 20 degrees left and right of center. The oscillating mechanism shall have a disconnect feature to allow for manual horizontal rotation.

The monitor shall include an integral safety shut off valve that will automatically shut down the water flow in the event control of the monitor is lost. The water flow is controlled by a six-position detent, turbulence free slide valve. The detent flow control shall also function as the reset for the safety shut off valve to resume water flow.

The 2-1/2” (64 mm) water inlet shall pivot up and down to allow for stability on uneven surfaces. The discharge has vertical elevation travel between 10 and 40 degrees above horizontal with a ball and socket joint. The same ball and socket joint shall allow for horizontal adjustment of 20 degrees left and right of center.

The monitor shall have folding stabilization legs with carbide tips, which are concealed in the carry and stow positions. An integral carrying handle that also functions as an attachment point for the included anchor strap shall be provided. For corrosion resistance, the monitor shall be constructed from hardcoat anodized aluminum alloy and have a blue powder coat interior and exterior finish.

The monitor shall be configured with a 2-1/2” (64 mm) female NH swivel inlet and a 2-1/2” male NH rigid outlet with a flow rating of 500 GPM (2000 l/min).

Max-Force nozzle tip model number MD12A dual pressure automatic nozzle shall have a knob located at the front of the nozzle to allow for pressure rating adjustments of 100 or 55 PSI (7 or 4 bar) and a flow range of 100-500 GPM (400-2000 l/min).

The nozzle design shall allow for straight stream through dense wide fog patterns and be able to be flushed without shutting down. The ribbed rubber bumper shall allow for stream shape adjustment. For corrosion resistance and durability, the nozzle shall be constructed from hardcoat anodized aluminum alloy, a protective rubber bumper with fog teeth, and reflective labeling. The nozzle shall have a 2-1/2” (64 mm) female NH swivel rocker lug coupling inlet.

The monitor and nozzle shall each have a unique serial number and all components shall be covered by a five-year warranty.