500 GPM REMOTE CONTROL MONITOR

Task Force Tips Tornado model # Y2-E03A-S electric remote-controlled monitor shall be installed. The monitor shall be controlled by a monitor mounted operator station with functions that control rotation, elevation, and nozzle patterns, oscillate, park, auxiliary 1 and auxiliary 2. The monitor shall have a flow capability of up to 500 GPM with no more than 19 PSI loss, maximum operating pressure of 200 PSI.

The monitor shall have the following travel capabilities: horizontal rotation with travel 170 degrees left and right of center, with infinitely adjustable rotation stops; vertical travel 135 degrees with field changeable vertical stops that can be adjusted using stop discs. Each disc reduces travel by 13 degrees. The monitor shall have seals on the vertical and horizontal rotational joints to prevent intrusion of foreign substances. The mechanical ingress protection rating for the ball races and gears shall be IP66/IP67.

The electrical components for the monitor shall be waterproof and utilize current limiting and position encoders to protect the drive train at the ends of travel. Monitor shall have waterproof plug for power and control cable connection for easy removal. An electrical connection for a TFT remote control nozzle shall be provided. The monitor shall be compatible with optional wired and wireless control panels and monitor position display. Electrical enclosure systems shall have a rating of IP66/IP67 per IEC 65029.

For resistance to corrosion the monitor shall be constructed from hardcoat anodized aluminum with a black powder coat exterior finish.

The monitor shall be configured with a 3” ANSI 150 flange inlet and 1-1/2" male BSP outlet. The unit shall have a unique serial number and be covered by a five-year warranty.