500 GPM REMOTE CONTROL MONITOR

Task Force Tips Tornado model # Y2-E12A electric remote controlled monitor shall be installed. The monitor shall be controlled by a monitor mounted operator station with functions that control rotation, elevation and nozzle patterns, oscillate, park, auxiliary 1 and auxiliary 2.

The monitor shall have the following travel capabilities: full horizontal rotation with travel 185 degrees left and right of center, full 135 degrees of vertical travel with field changeable vertical stops at 45 degrees above and 20 degrees below horizontal, field changeable rotation stops shall be provided 90 degrees left and right of center, flow capability of 500 GPM with no more than 19 PSI loss, maximum operating pressure of 200 PSI.

The electrical components for the monitor shall be waterproof and utilize current limiting and position encoders to protect the drive train at the ends of travel. Monitor shall have waterproof plug for power and control cable connection for easy removal. An electrical connection for a TFT remote control nozzle shall be provided. The monitor shall be compatible with optional wired and wireless control panels and monitor position display. The monitor shall be equipped with manual override knobs for use in the event of power failure. Electrical enclosure systems shall have a rating of IP66/IP67 per IEC 65029.

For resistance to corrosion the monitor shall be constructed from hardcoat anodized aluminum with a silver powder coat interior and exterior finish.

The monitor shall be configured with a 2-1/2" female NH swivel inlet quick disconnect with locking pin and 2-1/2" male BSP outlet. The unit shall have a unique serial number and be covered by a five-year warranty.