1250 GPM FIXED LOCATION MONITOR

Task Force Tips Monsoon model # Y4-M25A-Z manually controlled monitor shall be provided. The monitor shall operate with dual aluminum crank handles which control stainless steel worm gears for rotation and elevation adjustment.

The monitor shall have the following capabilities:

Full horizontal rotation with continuous 360 degree travel;

135 degrees of vertical travel from 45 degrees below and 90 degrees above horizontal;

Field changeable elevation stops at 30 and 45 degrees above horizontal and 30 degrees below horizontal;

Field changeable rotation stops shall be provided at 45, 90 and 135 degrees left and/or right of center;

Flow capability of 1250 GPM with a friction loss of no more than 6 PSI;

Maximum operating pressure of 200 PSI.

For resistance to corrosion the monitor shall be constructed from hardcoat anodized aluminum with an American red powder coat interior and exterior finish. A threaded port for an optional pressure gauge shall be provided. The unit shall have a unique serial number and be covered by a five-year warranty. Monitor shall be FM approved.

The monitor shall be designed with a unique waterway that minimizes the path of travel, reduces friction loss and turbulence, and produces a far reaching water stream. The monitor shall be configured with a 4" ANSI 150 flange inlet and 2-1/2" male NH outlet.